# PIF Preconstruction Risk Scan

# This sample is an anonymized composite based on several hospital projects I’ve reviewed. It reflects the type of issues I typically identify in pre‑tender packages — shutdown sequencing, infection‑control gaps, and cross‑discipline contradictions. I didn’t use any confidential client material, but the format and depth are exactly what you’d receive.

- Executive Summary

The tender package is generally well‑assembled, but several coordination gaps and constructability risks should be addressed before release.

Key issues include unclear shutdown sequencing, missing infection‑control notes, and conflicting mechanical/electrical responsibilities.

Overall Risk Level: Moderate–High

Recommended Action: Issue clarifications and addenda prior to tender release.

- High‑Priority Risks (Require Action Before Tender Release)

Shutdown Sequencing Not Defined

• 	Mechanical drawings reference “shutdowns as required,” but no schedule or window is provided.

• 	Hospital operations must confirm acceptable shutdown periods.

Impact: High — bidders will price conservatively or exclude.

Recommendation: Add a shutdown matrix to the tender.

  - Infection‑Control Requirements Missing

• 	No ICRA matrix included.

• 	No reference to negative‑pressure requirements in demolition areas.

Impact: High — major scope gap in a live hospital environment.

Recommendation: Include ICRA matrix and infection‑control notes in Division 01.

  - Conflicting Mechanical/Electrical Responsibilities

• 	Mechanical sheet M‑402 shows VFDs supplied by mechanical.

• 	Electrical sheet E‑203 shows VFDs supplied by electrical.

Impact: Medium — bidders will double‑carry or exclude.

Recommendation: Clarify responsible trade.

- Drawing & Specification Coherence Issues

Issue Discipline Impact Recommendation

Missing demolition notes on M‑101 Mechanical Medium Add demolition scope to match architectural

Architectural finish schedule Architectural Medium Provide full finish schedule

incomplete

Electrical panel schedules missing Electrical High Include panel schedules before tender

Phasing notes contradict drawing Multiple High Rewrite phasing notes for clarity

sequencing

- PIF Healthcare Risk Map (Text Excerpt)

High-Risk Zones:

- Mechanical Room 2B — shutdown coordination

- Corridor 2C — infection-control containment

- Electrical Room 2E — temporary power routing

Moderate-Risk Zones:

- Rooftop — crane access and staging

- Basement mechanical — temporary cooling requirements

- Pre-Release Addenda & Clarification List

Addenda Required

- Add shutdown matrix

- Add ICRA matrix

- Clarify VFD supply responsibility

- Add temporary works requirements

- Provide missing panel schedules

- Provide complete finish schedule

Clarifications

- Confirm access route for equipment removal

- Confirm after-hours work requirements

- Confirm infection-control staging areas

.